## Cover
Waterloo Road Pump Station
Instrument index and equipment list
Document number | WRPS-INS-001
Revision | A
Date | 11 August 2026
Status | Issued for demonstration
Prepared by | C. Huang
Checked by | -
Approved by | -
Parent documents | WRPS-PRO-001 Process Basis of Design; WRPS-DRG-001 P&ID
Child documents | WRPS-CTL-002 Functional Design Specification (to be issued)
Revision history
Rev | Date | Description | Prepared | Checked | Approved
A | 11 Aug 2026 | First issue - demonstration environment | C. Huang | - | -
Summary - live counts from the sheets in this workbook
Instrument tags | 34
Equipment tags | 20
Analogue inputs (AI) | 12
Digital inputs (DI) | 15
Serial / network points | 1
Local indication only (no I/O) | 6
Counts update automatically when rows are added or removed. I/O counts exclude spare capacity; refer to the Legend sheet for the spare I/O allowance to be applied when sizing PLC cards.

## Instrument index
Waterloo Road Pump Station
Instrument index
WRPS-INS-001 Rev A - 11 August 2026 - Issued for demonstration
Tag | Loop | Service description | Instrument type | Location | P&ID ref | Process range | Alarm / trip setpoint | Signal | I/O type | Power | Manufacturer / model | Notes
Wet well WW-101 and overflow structure
LIT-101 | 101 | Wet well level | Radar level transmitter, non-contact | Wet well headspace | WRPS-DRG-001 | 0 - 7.0 m | High 5.20 m | 4-20 mA HART | AI | 24 V DC | To be selected | Primary level measurement. All start, stop and speed control derive from this instrument.
LSHH-102 | 102 | Wet well high high level | Vibrating fork level switch | Wet well, 5.50 m | WRPS-DRG-001 | - | 5.50 m rising | Volt free NC | DI | 24 V DC | To be selected | Hardwired to VSD safety circuit. Must operate independently of PLC and of LIT-101.
LSLL-103 | 103 | Wet well low low level | Vibrating fork level switch | Wet well, 0.60 m | WRPS-DRG-001 | - | 0.60 m falling | Volt free NC | DI | 24 V DC | To be selected | Hardwired dry run protection. Fail safe on loss of supply.
LSH-104 | 104 | Overflow structure spill detection | Float level switch | Overflow structure | WRPS-DRG-001 | - | Weir crest 6.00 m | Volt free NO | DI | 24 V DC | To be selected | Spill event detection. Start and end time to be logged for reporting.
Inlet gravity main
FE-201 | 201 | Inlet flow element | Electromagnetic flow tube, DN600 | Inlet chamber | WRPS-DRG-001 | 0 - 400 L/s | - | - | - | - | To be selected | Requires full bore flow at the measurement point. Refer assumption A05 in WRPS-PRO-001.
FIT-201 | 201 | Inlet flow | Electromagnetic flow transmitter | Inlet chamber | WRPS-DRG-001 | 0 - 400 L/s | High 300 L/s | 4-20 mA HART | AI | 240 V AC | To be selected | Inflow measurement. Cross check against volumetric rate of change of LIT-101.
Common discharge manifold and rising main
PI-303 | 303 | Manifold pressure, local indication | Bourdon pressure gauge, 100 mm | Valve chamber | WRPS-DRG-001 | 0 - 1000 kPa | - | - | - | - | To be selected | Local indication for maintenance. No signal to control system.
FE-301 | 301 | Discharge flow element | Electromagnetic flow tube, DN400 | Valve chamber | WRPS-DRG-001 | 0 - 400 L/s | - | - | - | - | To be selected | Straight length requirements to be confirmed against final valve chamber layout.
FIT-301 | 301 | Common discharge flow | Electromagnetic flow transmitter | Valve chamber | WRPS-DRG-001 | 0 - 400 L/s | Low 50 L/s with pump running | 4-20 mA HART | AI | 240 V AC | To be selected | Pumped volume for mass balance against FIT-201 and for pump performance monitoring.
PIT-302 | 302 | Discharge manifold pressure | Pressure transmitter | Valve chamber | WRPS-DRG-001 | 0 - 600 kPa | High 480 kPa | 4-20 mA HART | AI | 24 V DC | To be selected | System head monitoring. Basis for detecting rising main obstruction.
Pump PU-301
PIT-311 | 311 | PU-301 discharge pressure | Pressure transmitter | Pump riser, valve chamber | WRPS-DRG-001 | 0 - 600 kPa | Low 150 kPa with pump running | 4-20 mA HART | AI | 24 V DC | To be selected | Confirms delivery on start. Detects closed isolation valve or blocked impeller.
TE-312 | 312 | PU-301 motor winding temperature | PTC thermistor set, embedded | Motor stator winding | WRPS-DRG-001 | - | Trip 140 deg C | Volt free NC | DI | 24 V DC | Pump supplier | Supplied with pump. Trips the affected unit and locks out until manual reset.
MSE-313 | 313 | PU-301 seal chamber leak detection | Conductivity probe | Pump seal chamber | WRPS-DRG-001 | - | Water ingress detected | Volt free NO | DI | 24 V DC | Pump supplier | Alarm only. Unit remains available and is flagged for service.
VE-314 | 314 | PU-301 bearing vibration | Accelerometer with transmitter | Pump bearing housing | WRPS-DRG-001 | 0 - 25 mm/s RMS | High 7.1, high high 11.0 mm/s | 4-20 mA | AI | 24 V DC | To be selected | Alarm on high. Trip the affected unit on high high.
PI-316 | 316 | PU-301 riser pressure, local indication | Bourdon pressure gauge, 100 mm | Pump riser, valve chamber | WRPS-DRG-001 | 0 - 1000 kPa | - | - | - | - | To be selected | Local indication for maintenance. No signal to control system.
Pump PU-302
PIT-321 | 321 | PU-302 discharge pressure | Pressure transmitter | Pump riser, valve chamber | WRPS-DRG-001 | 0 - 600 kPa | Low 150 kPa with pump running | 4-20 mA HART | AI | 24 V DC | To be selected | Confirms delivery on start. Detects closed isolation valve or blocked impeller.
TE-322 | 322 | PU-302 motor winding temperature | PTC thermistor set, embedded | Motor stator winding | WRPS-DRG-001 | - | Trip 140 deg C | Volt free NC | DI | 24 V DC | Pump supplier | Supplied with pump. Trips the affected unit and locks out until manual reset.
MSE-323 | 323 | PU-302 seal chamber leak detection | Conductivity probe | Pump seal chamber | WRPS-DRG-001 | - | Water ingress detected | Volt free NO | DI | 24 V DC | Pump supplier | Alarm only. Unit remains available and is flagged for service.
VE-324 | 324 | PU-302 bearing vibration | Accelerometer with transmitter | Pump bearing housing | WRPS-DRG-001 | 0 - 25 mm/s RMS | High 7.1, high high 11.0 mm/s | 4-20 mA | AI | 24 V DC | To be selected | Alarm on high. Trip the affected unit on high high.
PI-326 | 326 | PU-302 riser pressure, local indication | Bourdon pressure gauge, 100 mm | Pump riser, valve chamber | WRPS-DRG-001 | 0 - 1000 kPa | - | - | - | - | To be selected | Local indication for maintenance. No signal to control system.
Pump PU-303
PIT-331 | 331 | PU-303 discharge pressure | Pressure transmitter | Pump riser, valve chamber | WRPS-DRG-001 | 0 - 600 kPa | Low 150 kPa with pump running | 4-20 mA HART | AI | 24 V DC | To be selected | Confirms delivery on start. Detects closed isolation valve or blocked impeller.
TE-332 | 332 | PU-303 motor winding temperature | PTC thermistor set, embedded | Motor stator winding | WRPS-DRG-001 | - | Trip 140 deg C | Volt free NC | DI | 24 V DC | Pump supplier | Supplied with pump. Trips the affected unit and locks out until manual reset.
MSE-333 | 333 | PU-303 seal chamber leak detection | Conductivity probe | Pump seal chamber | WRPS-DRG-001 | - | Water ingress detected | Volt free NO | DI | 24 V DC | Pump supplier | Alarm only. Unit remains available and is flagged for service.
VE-334 | 334 | PU-303 bearing vibration | Accelerometer with transmitter | Pump bearing housing | WRPS-DRG-001 | 0 - 25 mm/s RMS | High 7.1, high high 11.0 mm/s | 4-20 mA | AI | 24 V DC | To be selected | Alarm on high. Trip the affected unit on high high.
PI-336 | 336 | PU-303 riser pressure, local indication | Bourdon pressure gauge, 100 mm | Pump riser, valve chamber | WRPS-DRG-001 | 0 - 1000 kPa | - | - | - | - | To be selected | Local indication for maintenance. No signal to control system.
Station environmental and safety monitoring
AIT-401 | 401 | Wet well headspace hydrogen sulphide | Electrochemical gas detector | Wet well headspace | - | 0 - 50 ppm | High 10 ppm, high high 20 ppm | 4-20 mA | AI | 24 V DC | To be selected | Confined space entry monitoring. Not shown on WRPS-DRG-001.
AIT-402 | 402 | Valve chamber flammable gas | Catalytic bead detector | Valve chamber | - | 0 - 100 % LEL | High 10 %, high high 20 % LEL | 4-20 mA | AI | 24 V DC | To be selected | Confined space entry monitoring. Not shown on WRPS-DRG-001.
LSH-403 | 403 | Valve chamber sump high level | Float level switch | Valve chamber sump | - | - | Sump high | Volt free NO | DI | 24 V DC | To be selected | Detects chamber flooding from a leaking gland or valve.
LSH-404 | 404 | Switchroom flood detection | Conductive water detection strip | Switchroom floor | - | - | Water present | Volt free NO | DI | 24 V DC | To be selected | Protects switchboard and control panel.
Electrical supply and station status
JI-501 | 501 | Station incomer energy metering | Multifunction power meter | MSB-001 | - | 0 - 400 kW, kWh totalised | - | Modbus TCP | Serial | 240 V AC | To be selected | Station energy consumption. Required for cost attribution against tariff periods.
XA-502 | 502 | Mains supply failure | Voltage relay, auxiliary contact | MSB-001 | - | - | Loss of one or more phases | Volt free NC | DI | 24 V DC | Switchboard supplier | Triggers changeover to standby supply at GEN-001.
XA-503 | 503 | Standby generator connected and running | Auxiliary contact | MSB-001 | - | - | Generator on load | Volt free NO | DI | 24 V DC | Switchboard supplier | Station capacity may be restricted while on generator. To be confirmed.
XA-504 | 504 | Site security, switchroom door | Magnetic door switch | Switchroom door | - | - | Door open | Volt free NC | DI | 24 V DC | To be selected | Unauthorised access alarm.
XA-505 | 505 | Surge diverter fault | Auxiliary contact | MSB-001 | - | - | Diverter expended | Volt free NC | DI | 24 V DC | Switchboard supplier | Maintenance alarm only, no process action.
Notes: (1) All signals terminate at PLC-001 unless stated otherwise. (2) Setpoints shown are design values from WRPS-PRO-001 Section 6 and are to be confirmed during alarm rationalisation. (3) Instruments marked 'To be selected' require model selection before the loop drawings can be issued. (4) AIT-401, AIT-402, LSH-403, LSH-404 and the XA and JI series are not shown on WRPS-DRG-001 and are recorded here only.

## Equipment list
Waterloo Road Pump Station
Equipment list
WRPS-INS-001 Rev A - 11 August 2026 - Issued for demonstration
Tag | Description | Type / configuration | Duty | Rated capacity | Drive / power | Material | P&ID ref | Notes
Civil and structural
WW-101 | Wet well | Rectangular in-ground concrete chamber, 12.0 m x 10.0 m | Continuous | 120 m2 plan, 6.0 m operating depth, 720 m3 to spill | - | Reinforced concrete with protective lining | WRPS-DRG-001 | Working volume 360 m3 between 1.00 m and 4.00 m. Emergency storage 240 m3 above 4.00 m.
OF-102 | Overflow weir and emergency relief structure | Side weir with relief chamber | Emergency only | Weir crest 6.00 m | - | Reinforced concrete | WRPS-DRG-001 | Spill events detected by LSH-104 and logged.
VC-103 | Valve chamber | In-ground concrete chamber | Continuous | Houses manifold, valves and flow metering | - | Reinforced concrete | WRPS-DRG-001 | Confined space. Gas detection AIT-402 and sump switch LSH-403 installed.
Pumps and drives
PU-301 | Transfer pump 1 | Submersible non-clog centrifugal, guide rail mounted | 2 duty + 1 standby (3 x 50%) | 120 L/s at 32 m total head | 75 kW, 415 V, 3 phase, variable speed | Cast iron casing, duplex stainless shaft | WRPS-DRG-001 | All three units functionally interchangeable. Minimum speed 38 Hz set by 22 m static lift.
PU-302 | Transfer pump 2 | Submersible non-clog centrifugal, guide rail mounted | 2 duty + 1 standby (3 x 50%) | 120 L/s at 32 m total head | 75 kW, 415 V, 3 phase, variable speed | Cast iron casing, duplex stainless shaft | WRPS-DRG-001 | All three units functionally interchangeable. Minimum speed 38 Hz set by 22 m static lift.
PU-303 | Transfer pump 3 | Submersible non-clog centrifugal, guide rail mounted | 2 duty + 1 standby (3 x 50%) | 120 L/s at 32 m total head | 75 kW, 415 V, 3 phase, variable speed | Cast iron casing, duplex stainless shaft | WRPS-DRG-001 | All three units functionally interchangeable. Minimum speed 38 Hz set by 22 m static lift.
VSD-301 | Variable speed drive, pump 1 | Voltage source inverter with integral EMC filter | One per pump | 75 kW continuous, 38 - 50 Hz operating range | 415 V, 3 phase | IP54 enclosure, switchroom mounted | WRPS-DRG-001 | No fixed speed or DOL starters at this station. Hardwired LSLL-103 and LSHH-102 interlocks act on the drive safety circuit.
VSD-302 | Variable speed drive, pump 2 | Voltage source inverter with integral EMC filter | One per pump | 75 kW continuous, 38 - 50 Hz operating range | 415 V, 3 phase | IP54 enclosure, switchroom mounted | WRPS-DRG-001 | No fixed speed or DOL starters at this station. Hardwired LSLL-103 and LSHH-102 interlocks act on the drive safety circuit.
VSD-303 | Variable speed drive, pump 3 | Voltage source inverter with integral EMC filter | One per pump | 75 kW continuous, 38 - 50 Hz operating range | 415 V, 3 phase | IP54 enclosure, switchroom mounted | WRPS-DRG-001 | No fixed speed or DOL starters at this station. Hardwired LSLL-103 and LSHH-102 interlocks act on the drive safety circuit.
Valves and pipework
NRV-311 | Check valve, pump 1 riser | Swing check, resilient seated | One per pump | DN300, PN16 | - | Ductile iron body, EPDM seat | WRPS-DRG-001 | Prevents reverse flow from the manifold when the unit is stopped.
NRV-321 | Check valve, pump 2 riser | Swing check, resilient seated | One per pump | DN300, PN16 | - | Ductile iron body, EPDM seat | WRPS-DRG-001 | Prevents reverse flow from the manifold when the unit is stopped.
NRV-331 | Check valve, pump 3 riser | Swing check, resilient seated | One per pump | DN300, PN16 | - | Ductile iron body, EPDM seat | WRPS-DRG-001 | Prevents reverse flow from the manifold when the unit is stopped.
IV-312 | Isolation valve, pump 1 riser | Manual resilient seated gate valve | One per pump | DN300, PN16 | Handwheel operated | Ductile iron body, EPDM seat | WRPS-DRG-001 | Manual only. No position feedback to the control system, so a closed valve is detected by PIT on the affected riser.
IV-322 | Isolation valve, pump 2 riser | Manual resilient seated gate valve | One per pump | DN300, PN16 | Handwheel operated | Ductile iron body, EPDM seat | WRPS-DRG-001 | Manual only. No position feedback to the control system, so a closed valve is detected by PIT on the affected riser.
IV-332 | Isolation valve, pump 3 riser | Manual resilient seated gate valve | One per pump | DN300, PN16 | Handwheel operated | Ductile iron body, EPDM seat | WRPS-DRG-001 | Manual only. No position feedback to the control system, so a closed valve is detected by PIT on the affected riser.
IM-402 | Inlet gravity main | Gravity sewer | Continuous | DN600, 1.06 m/s at PWWF | - | To be confirmed | WRPS-DRG-001 | Flow metering FE-201 and FIT-201 require a full bore section. Refer assumption A05.
RM-401 | Rising main | Pumped discharge main | Continuous | DN400, 0.96 m/s at one pump, 2.86 m/s at three pumps | - | To be confirmed | WRPS-DRG-001 | Downstream storage assumed unconstrained. No downstream level feedback provided.
Electrical and control
MSB-001 | Main switchboard | Form 3b switchboard with generator changeover | Continuous | 400 A, 415 V, 3 phase | 415 V supply | Powder coated steel, IP54 | - | Houses JI-501 metering and the XA series status contacts.
PLC-001 | Station control panel | PLC and I/O panel with operator interface | Continuous | I/O count per Instrument index sheet | 240 V AC with 24 V DC distribution | Powder coated steel, IP54 | WRPS-DRG-001 | Card sizing to include the spare I/O allowance on the Legend sheet.
GEN-001 | Standby generator connection point | External socket outlet with changeover | Emergency only | To be confirmed against three-pump load | 415 V, 3 phase | Stainless steel enclosure | - | Whether all three pumps may run on generator is unconfirmed and may restrict capacity.
Notes: (1) Pump duty point and motor rating are from WRPS-PRO-001 Section 3. (2) Materials shown are indicative and require confirmation against a wastewater compatibility assessment. (3) Items marked 'To be confirmed' are open and are tracked in the assumptions register in WRPS-PRO-001 Section 9.

## Legend
Legend and conventions
Applies to the Instrument index and Equipment list sheets
Tag numbering
Format | Function letters followed by a three digit loop number, per ISA-5.1.
100 series | Wet well WW-101 and overflow structure.
200 series | Inlet gravity main.
300 series | Pumps, risers, discharge manifold and rising main. 31x = PU-301, 32x = PU-302, 33x = PU-303.
400 series | Station environmental and safety monitoring.
500 series | Electrical supply and station status.
Function letters used
A | Analysis
E | Element, primary sensing
F | Flow
H | High (as a modifier)
I | Indicate
J | Power
L | Level, or Low as a modifier
M | Moisture
P | Pressure
S | Switch
T | Temperature, or Transmit
V | Vibration
X | Unclassified status
Z | Position
I/O types
AI | Analogue input, 4-20 mA into the PLC.
DI | Digital input, volt free contact into the PLC.
Serial | Data read over a serial or network protocol, not a hardwired point.
- | Local indication only. No connection to the control system.
Spare I/O allowance for card sizing
Analogue inputs | 20 percent spare, minimum two spare channels per card.
Digital inputs | 20 percent spare, minimum four spare channels per card.
Digital outputs | 20 percent spare.
Note | Counts on the Cover sheet are installed points only and exclude this allowance.
Status conventions
To be selected | Model or supplier not yet chosen. Blocks issue of loop drawings.
To be confirmed | Value adopted as an assumption. Tracked in WRPS-PRO-001 Section 9.